## Cables
DC Cable Sizing |  |  |  | AC Cable Sizing
Parameter | Value | Unit | Remarks | Parameter | Value | Unit | Remarks
Each String Current | 13.7 | A | Already we got it from PV string calc. file | Inverter Output | 5 | kW | Already we got it from PV string calc. file
Each String voltage | 196.9 | V | Already we got it from PV string calc. file | Grid line voltage | 230 | V | 1-phase. Technically its around 220 V though
Primary Cable selection | 4 | sq. mm | Cu material wire. Such cross-section is selected cause it is also consistent with module's specified cross-section | Approx. AC current | 21.7391 | A | Using I = P/V formula, This is the approx. current level that inverter will supply to overall residential load to maintain 230V
Assumed Cable length (one way) | 25 | m | Each module is 1.05 m wide, so 25 m cable is sufficient for 12 modules in one way. So 2 way total cable required is 50 m | Primary Cable selection | 6 | sq.mm | Cu material wire. Such cross section is selected to get standard rated cables in market
Copper Ressistivity | 0.0175 | ohm.mm_sq / m |  | Cable rating | 32 | A | Selected a higher rated cable than actual load (2-pole MCB). A safe practice
Voltage drop in total cable | 2.9969 | V | Calculated using [V = (2*I*L*ro) / A] formula, where I=13.7, L=25, ro=0.0175, A=4 | Cable length (one way) | 20 | m | One way length is 20m. So total cable length becomes 40m
Voltage drop (%) | 1.522 | % | For priliminary design, 1.5% drop is reasonable | Voltage drop in total cable | 2.5362 | V | Calculated using [V = (2*I*L*ro) / A] formula, where I=21.7, L=20, ro=0.0175, A=6
|  |  |  | Voltage drop (%) | 1.1027 | % | For priliminary design, 1.1% drop is in acceptable range

## Protection
Protection Measurements Chart
Location | Protection | Preliminary Selection
PV String | DC Isolator | DC-rated Isolator
PV DC side | DC SPD | Type II DC SPD
Inverter AC side | AC Isolator | 2-pole AC Isolator
Inverter AC side | MCB | 32 A, 2P preliminary
AC side | SPD | Type II AC SPD
Battery side | Battery Protection | DC fuse/isolator, rated per battery/inverter
Backup output | Protection | Dedicated backup DB with MCBs
Main Supply | MCB | Existing/main DB protection arrangement
Earthing | 6 sq.mm Cu wire | Protective conductor. The rating and resistance depends on Electrical code & site condition